## 18.03.26
FURNACE FLAME TEMPERATURE MAPPING
UNIT : 5 |  |  | Date :- 18/03/2026 |  |  | Time :- 9:00
Load (MW) : - | 495 |  | Total Coal flow (TPH) :- 353 |  |  | 355
Coal Mills in Service : | 6 | ABDEFG | Total Air flow (TPH) :- 1602 |  |  | 1655 |  | 50
Oil Guns in Service : |  |  | Burner Tilt Position (Deg) :- 10,27,24,17 |  |  | 34,32,31,34
( Flame Temp. in 0C - Average ) Instrument Used : Chino Infrared Thermometer - Model - IR HASNE
ELEVATION | CORNER 1 | CORNER 2 | CORNER 3 | CORNER 4 | AVERAGE |  | ELEVATION
58.35 | 1078 | 1200 | 1100 | 1290 | 1167 |  | 58.4 M
49.2 | 1134 | 1245 | 1111 | 1167 | 1164.25 |  | 49.2 M
46.2 | 1185 | 1198 | 1176 | 1179 | 1184.5 |  | 46.2 M
42.2 | 1221 | 1217 | 1181 | 1190 | 1202.25 |  | 42.2 M
38.65 | 1172 | 1193 | 1156 | 1166 | 1171.75 |  | 38.65 M
35 | 1138 | 1151 | 1122 | 1125 | 1134 |  | GH / 35.0 M
31.4 | 1072 | 1060 | 1041 | 1062 | 1058.75 |  | EF / 31.4 M
27.8 | 1028 | 1035 | 1016 | 1024 | 1025.75 |  | CD / 27.8 M
24.2 | 1013 | 1006 | 1020 | 1010 | 1012.25 |  | AB / 24.2 M
NOTE:- YELLOW FOR HIGHER TEMPERATURE AND GREEN FOR LOWER TEMPERATURE
Boiler & Mill Parameters : |  | L | R |  |  |  | L | R
Main Steam Pressure (Kg/cm2) : |  | 164 |  | FG Temp after DPSH (L/R ) 0C : |  |  | 853 | 817
Main Steam Flow (TPH) : |  | 1518 |  | FG Temp after PSH (L/R ) 0C : |  |  | 815 | 712
Superheat Spray (TPH) : |  | 35 | 17 | FG Temp after RH (L/R ) 0C : |  |  | 675 | 607
Re-heat Spray (TPH) : |  | 4 | 5 | FG Temp after HSH (L/R) 0C : |  |  | 487 | 472 | 340
O2 at APH Inlet (PCR) % |  | 3.6 | 2.2 | FG Temp after Economizer (L/R) 0C : |  |  | 350 | 358
Wind Box DP - A / B (mmwcl) : |  | 84 | 92 | FG Temp after APH (L/R) 0C : |  |  | 137 | 140
Total PA flow (TPH) |  | 768
Coal Mill Parameters : -
COAL MILLS | Coal Mill - A | Coal Mill - B | Coal Mill - C | Coal Mill - D | Coal Mill - E | Coal Mill - F | Coal Mill - G | Coal Mill - H
Coal Flow (TPH) | 61 | 59 |  | 60 | 60 | 57 | 58
PA Flow (TPH) | 115 | 115 |  | 110 | 114 | 114 | 114
Mill DP (mmwcl) | 13 | -2 |  | 363 | 0 | 142 | 13
Mill Outlet Temp (0C) | 65 | 71 |  | 79 | 70 | 67 | 69
Mill Current (Amp) | 62 | 54 |  | 58 | 59 | 54 | 56